## ACSR Drake
CABLE
Name	ACSR Drake
Area-Physical	[in^2]	0.7264
Diameter	[in]	1.108
Unit Weight	[lb/ft]	1.094
Rated Strength	[lbs]	31500
Ref Temp	[°F]	70

SHELL
Thermal Coefficient	[/°F*100]	0.00128
Modulus-Tension	[lbs/in^2/100]	64000
Modulus-Compression	[lbs/in^2/100]	1500
Coefficients-Stress/Strain	[lbs/in^2]	-1213	44308.1	-14004.4	-37618	30676
Limit Stress/Strain	[lbs/in^2]	14655
Coefficients-Creep	[lbs/in^2]	-544.8	21426.8	-18842.2	5495	0
Limit Creep	[lbs/in^2]	14655

CORE
Thermal Coefficient	[/°F*100]	0.00064
Modulus-Tension	[lbs/in^2/100]	37000
Modulus-Compression	[lbs/in^2/100]	0
Coefficients-Stress/Strain	[lbs/in^2]	-69.3	38629	3998.1	-45713	27892
Limit Stress/Strain	[lbs/in^2]	16273.9
Coefficients-Creep	[lbs/in^2]	47.1	36211.3	12201.4	-72392	46338
Limit Creep	[lbs/in^2]	16273.9

## InitialPolynomial
Reference / Temp	Loading / Temp		X-Section / Area	Compress		Tension / Modulus

70	70		0.7264	YES		64000	4648960

Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients - Stress/Strain					Coefficients - Creep
			a0	a1	a2	a3	a4	a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-55000	35000	-5000	0	0	0	0	0

Point	Unload	Stretch	Extrap
x	0		0
y	0
								Strain / Load (lbs)

Strain	Stress	Load	Slope	Stress	Load	Slope
(%)	(psi)	(lbs)	(lbs)	(psi)	(lbs)	(lbs)
-0.200	-11349.6	-8244.4	5133331	0.0	0.0	0
-0.100	-5016.3	-3643.8	4095305	0.0	0.0	0
0.000	0.0	0.0	3218540	0.0	0.0	0
0.100	3915.3	2844.1	2494320	0.0	0.0	0
0.200	6933.6	5036.6	1913926	0.0	0.0	0
0.300	9246.9	6717.0	1468643	0.0	0.0	0
0.400	11035.2	8016.0	1149753	0.0	0.0	0
0.500	12466.5	9055.7	948540	0.0	0.0	0

## TemperatureShift
Reference / Temp	Loading / Temp		X-Section / Area	Compress		Tension / Modulus

70	70		0.7264	YES		64000	4648960

Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients - Stress/Strain					Coefficients - Creep
			a0	a1	a2	a3	a4	a0	a1	a2	a3	a4
150	0.00128	0.1024	0	44308.1	-55000	35000	-5000	0	0	0	0	0

Point	Unload	Stretch	Extrap
x	0		0
y	0
								Strain / Load (lbs)

Strain	Stress	Load	Slope	Stress	Load	Slope
(%)	(psi)	(lbs)	(lbs)	(psi)	(lbs)	(lbs)
-0.200	-11349.6	-8244.4	5133331	-19438.0	-14119.7	0
-0.100	-5016.3	-3643.8	4095305	-11519.7	-8367.9	0
0.000	0.0	0.0	3218540	-5152.0	-3742.4	0
0.100	3915.3	2844.1	2494320	-106.7	-77.5	0
0.200	6933.6	5036.6	1913926	3832.6	2784.0	0
0.300	9246.9	6717.0	1468643	6870.2	4990.5	0
0.400	11035.2	8016.0	1149753	9198.3	6681.6	0
0.500	12466.5	9055.7	948540	10997.1	7988.3	0

## Stretch
Reference / Temp	Loading / Temp		X-Section / Area	Compress		Tension / Modulus

70	70		0.7264	YES		64000	4648960

Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients - Stress/Strain					Coefficients - Creep
			a0	a1	a2	a3	a4	a0	a1	a2	a3	a4
150	0.00128	0.1024	0	44308.1	-55000	35000	-5000	0	0	0	0	0

Point	Unload	Stretch	Extrap
x	0.19068910035793	0.350000	0.19068910035793
y	0	7406.3
								Strain / Load (lbs)

Strain	Stress	Load	Slope	Stress	Load	Slope
(%)	(psi)	(lbs)	(lbs)	(psi)	(lbs)	(lbs)
-0.200	-11349.6	-8244.4	5133331	0.0	0.0	0
-0.100	-5016.3	-3643.8	4095305	0.0	0.0	0
0.000	0.0	0.0	3218540	0.0	0.0	0
0.100	3915.3	2844.1	2494320	0.0	0.0	0
0.200	6933.6	5036.6	1913926	0.0	0.0	0
0.300	9246.9	6717.0	1468643	0.0	0.0	0
0.400	11035.2	8016.0	1149753	0.0	0.0	0
0.500	12466.5	9055.7	948540	0.0	0.0	0

## Stretch-Creep
Reference / Temp	Loading / Temp		X-Section / Area	Compress		Tension / Modulus

70	70		0.7264	YES		64000	4648960

Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients - Stress/Strain					Coefficients - Creep
			a0	a1	a2	a3	a4	a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-55000	35000	-5000	0	30000	-50000	35000	-5000

Point	Unload	Stretch	Extrap
x	0.19068910035793	0.350000	0.19068910035793
y	0	7406.3
								Strain / Load (lbs)

Strain	Stress	Load	Slope	Stress	Load	Slope
(%)	(psi)	(lbs)	(lbs)	(psi)	(lbs)	(lbs)
-0.200	-11349.6	-8244.4	5133331	-8288.0	-6020.4	3948710
-0.100	-5016.3	-3643.8	4095305	-3535.5	-2568.2	2983325
0.000	0.0	0.0	3218540	0.0	0.0	2179200
0.100	3915.3	2844.1	2494320	2534.5	1841.1	1527619
0.200	6933.6	5036.6	1913926	4272.0	3103.2	1019866
0.300	9246.9	6717.0	1468643	5404.5	3925.8	647222
0.400	11035.2	8016.0	1149753	6112.0	4439.8	400973					Initial / Polynomial
0.500	12466.5	9055.7	948540	6562.5	4767.0	272400

									Everyday / Load

											Creep Polynomial

## Stretch-Load
Reference / Temp	Loading / Temp		X-Section / Area	Compress		Tension / Modulus

70	70		0.7264	YES		64000	4648960

Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients - Stress/Strain					Coefficients - Creep
			a0	a1	a2	a3	a4	a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-55000	35000	-5000	0	0	0	0	0

Point	Unload	Stretch	Extrap
x	0.19068910035793	0.350000	0.19068910035793
y	0	7406.3
								Strain / Load (lbs)

Strain	Stress	Load	Slope	Stress	Load	Slope
(%)	(psi)	(lbs)	(lbs)	(psi)	(lbs)	(lbs)
-0.200	-11349.6	-8244.4	5133331	0.0	0.0	0
-0.100	-5016.3	-3643.8	4095305	0.0	0.0	0
0.000	0.0	0.0	3218540	0.0	0.0	0			High / Load
0.100	3915.3	2844.1	2494320	0.0	0.0	0
0.200	6933.6	5036.6	1913926	0.0	0.0	0
0.300	9246.9	6717.0	1468643	0.0	0.0	0
0.400	11035.2	8016.0	1149753	0.0	0.0	0
0.500	12466.5	9055.7	948540	0.0	0.0	0

										Initial / Polynomial

## Components
Reference / Temp	Loading / Temp		X-Section / Area	Compress

70	70		0.7264	YES

Shell
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-14004.4	-37618	30676

Core
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4			Strain / Load (lbs)
70	0.00064	0	0	20000	3998.1	-45713	40000

Strain	Stress			Load			Slope
	No Adjustment			Compression Modification
	Core	Shell	Total	Core	Shell	Total	Core	Shell	Total
(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)
-0.200	-3410.4	-9071.8	-12482.1	-2477.3	-6589.7	-9067.0	845181	3226238	4071419
-0.100	-1910.3	-4530.2	-6440.5	-1387.6	-3290.7	-4678.4	1283475	3331106	4614581
0.000	0.0	0.0	0.0	0.0	0.0	0.0	1452800	3218540	4671340
0.100	1998.3	4256.2	6254.5	1451.5	3091.7	4543.3	1422889	2942021	4364910
0.200	3858.2	8049.6	11907.8	2802.6	5847.2	8649.8	1263477	2555026	3818503
0.300	5449.6	11264.8	16714.4	3958.6	8182.8	12141.3	1044298	2111035	3155333
0.400	6738.1	13860.3	20598.4	4894.5	10068.1	14962.6	835087	1663528	2498615
0.500	7785.4	15868.0	23653.4	5655.3	11526.5	17181.8	705578	1265984	1971562

## ComponentStretch-1
Reference / Temp	Loading / Temp		X-Section / Area	Compress

70	70		0.7264	YES

Shell
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-14004.4	-37618	30676

Core
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4			Strain / Load (lbs)
70	0.00064	0	0	20000	3998.1	-45713	40000

Strain	Stress			Load			Slope
	No Adjustment			Compression Modification
	Core	Shell	Total	Core	Shell	Total	Core	Shell	Total
(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)
-0.200	-3410.4	-9071.8	-12482.1	-2477.3	-6589.7	-9067.0	845181	3226238	4071419
-0.100	-1910.3	-4530.2	-6440.5	-1387.6	-3290.7	-4678.4	1283475	3331106	4614581
0.000	0.0	0.0	0.0	0.0	0.0	0.0	1452800	3218540	4671340
0.100	1998.3	4256.2	6254.5	1451.5	3091.7	4543.3	1422889	2942021	4364910
0.200	3858.2	8049.6	11907.8	2802.6	5847.2	8649.8	1263477	2555026	3818503
0.300	5449.6	11264.8	16714.4	3958.6	8182.8	12141.3	1044298	2111035	3155333
0.400	6738.1	13860.3	20598.4	4894.5	10068.1	14962.6	835087	1663528	2498615			Stretch Load
0.500	7785.4	15868.0	23653.4	5655.3	11526.5	17181.8	705578	1265984	1971562

## ComponentStretch-2
Reference / Temp	Loading / Temp		X-Section / Area	Compress

70	212		0.7264	YES

Shell
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
212	0.00128	0.18176	0	44308.1	-14004.4	-37618	30676

Core
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4			Strain / Load (lbs)
212	0.00064	0.09088	0	20000	3998.1	-45713	40000

Strain	Stress			Load			Slope
	No Adjustment			Compression Modification
	Core	Shell	Total	Core	Shell	Total	Core	Shell	Total
(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)
-0.200	-4067.9	-16211.5	-20279.4	-2954.9	-11776.0	-14731.0	845181	3226238	4071419
-0.100	-3300.9	-12561.2	-15862.1	-2397.8	-9124.5	-11522.3	1283475	3331106	4614581
0.000	-1747.5	-8256.7	-10004.3	-1269.4	-5997.7	-7267.1	1452800	3218540	4671340
0.100	182.7	-3694.3	-3511.6	132.7	-2683.6	-2550.8	1422889	2942021	4364910
0.200	2176.3	803.3	2979.6	1580.9	583.5	2164.4	1263477	2555026	3818503
0.300	4015.7	4987.0	9002.7	2917.0	3622.6	6539.6	1044298	2111035	3155333
0.400	5579.4	8681.4	14260.8	4052.9	6306.1	10359.0	835087	1663528	2498615
0.500	6841.9	11784.5	18626.4	4969.9	8560.3	13530.2	705578	1265984	1971562

## ReloadedLength
Reference / Temp	Loading / Temp		X-Section / Area	Compress					Reference / Temp	Loading / Temp		X-Section / Area	Compress

70	70		0.7264	YES					70	212		0.7264	YES

Shell					Shell
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients					Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4					a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-14004.4	-37618	30676				212	0.00128	0.18176	0	44308.1	-14004.4	-37618	30676

Core					Core
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients					Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4					a0	a1	a2	a3	a4		Strain / Load (lbs)
70	0.00064	0	0	20000	3998.1	-45713	40000				212	0.00064	0.09088	0	20000	3998.1	-45713	40000

Strain	Stress			Load			Slope				Strain	Stress			Load			Slope
	No Adjustment			Compression Modification					No Adjustment			Compression Modification
	Core	Shell	Total	Core	Shell	Total	Core	Shell	Total			Core	Shell	Total	Core	Shell	Total	Core	Shell	Total
(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)		(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)
-0.200	-3410.4	-9071.8	-12482.1	-2477.3	-6589.7	-9067.0	845181	3226238	4071419		-0.200	-4067.9	-16211.5	-20279.4	-2954.9	-11776.0	-14731.0	845181	3226238	4071419
-0.100	-1910.3	-4530.2	-6440.5	-1387.6	-3290.7	-4678.4	1283475	3331106	4614581		-0.100	-3300.9	-12561.2	-15862.1	-2397.8	-9124.5	-11522.3	1283475	3331106	4614581 / Load
0.000	0.0	0.0	0.0	0.0	0.0	0.0	1452800	3218540	4671340		0.000	-1747.5	-8256.7	-10004.3	-1269.4	-5997.7	-7267.1	1452800	3218540	4671340
0.100	1998.3	4256.2	6254.5	1451.5	3091.7	4543.3	1422889	2942021	4364910		0.100	182.7	-3694.3	-3511.6	132.7	-2683.6	-2550.8	1422889	2942021	4364910
0.200	3858.2	8049.6	11907.8	2802.6	5847.2	8649.8	1263477	2555026	3818503		0.200	2176.3	803.3	2979.6	1580.9	583.5	2164.4	1263477	2555026	3818503
0.300	5449.6	11264.8	16714.4	3958.6	8182.8	12141.3	1044298	2111035	3155333		0.300	4015.7	4987.0	9002.7	2917.0	3622.6	6539.6	1044298	2111035	3155333
0.400	6738.1	13860.3	20598.4	4894.5	10068.1	14962.6	835087	1663528	2498615		0.400	5579.4	8681.4	14260.8	4052.9	6306.1	10359.0	835087	1663528	2498615
0.500	7785.4	15868.0	23653.4	5655.3	11526.5	17181.8	705578	1265984	1971562		0.500	6841.9	11784.5	18626.4	4969.9	8560.3	13530.2	705578	1265984	1971562

				Δε

				εs			εf

## Reload-1
Reference / Temp	Loading / Temp		X-Section / Area	Compress

70	70		0.7264	YES

Shell
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-14004.4	-37618	30676

Core
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
70	0.00064	0	0	20000	3998.1	-45713	40000

Strain	Stress			Load			Slope
	No Adjustment			Compression Modification
	Core	Shell	Total	Core	Shell	Total	Core	Shell	Total
(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)
-0.200	-3410.4	-9071.8	-12482.1	-2477.3	-6589.7	-9067.0	845181	3226238	4071419
-0.100	-1910.3	-4530.2	-6440.5	-1387.6	-3290.7	-4678.4	1283475	3331106	4614581
0.000	0.0	0.0	0.0	0.0	0.0	0.0	1452800	3218540	4671340
0.100	1998.3	4256.2	6254.5	1451.5	3091.7	4543.3	1422889	2942021	4364910
0.200	3858.2	8049.6	11907.8	2802.6	5847.2	8649.8	1263477	2555026	3818503
0.300	5449.6	11264.8	16714.4	3958.6	8182.8	12141.3	1044298	2111035	3155333		TAVG-s
0.400	6738.1	13860.3	20598.4	4894.5	10068.1	14962.6	835087	1663528	2498615
0.500	7785.4	15868.0	23653.4	5655.3	11526.5	17181.8	705578	1265984	1971562

									εs

## Reload-2
Reference / Temp	Loading / Temp		X-Section / Area	Compress

70	70		0.7264	YES

Shell
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
70	0.00128	0	0	44308.1	-14004.4	-37618	30676

Core
Temp	Thermal / Coefficient	Thermal / Expansion	Coefficients
			a0	a1	a2	a3	a4
70	0.00064	0	0	20000	3998.1	-45713	40000

Strain	Stress			Load			Slope
	No Adjustment			Compression Modification
	Core	Shell	Total	Core	Shell	Total	Core	Shell	Total
(%)	(psi)	(psi)	(psi)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)	(lbs)
-0.200	-3410.4	-9071.8	-12482.1	-2477.3	-6589.7	-9067.0	845181	3226238	4071419
-0.100	-1910.3	-4530.2	-6440.5	-1387.6	-3290.7	-4678.4	1283475	3331106	4614581
0.000	0.0	0.0	0.0	0.0	0.0	0.0	1452800	3218540	4671340
0.100	1998.3	4256.2	6254.5	1451.5	3091.7	4543.3	1422889	2942021	4364910
0.200	3858.2	8049.6	11907.8	2802.6	5847.2	8649.8	1263477	2555026	3818503
0.300	5449.6	11264.8	16714.4	3958.6	8182.8	12141.3	1044298	2111035	3155333
0.400	6738.1	13860.3	20598.4	4894.5	10068.1	14962.6	835087	1663528	2498615
0.500	7785.4	15868.0	23653.4	5655.3	11526.5	17181.8	705578	1265984	1971562

									TAVG-f

									εf